## Calculator
Expansion Tank Sizing Procedure
900 | Sys Vol | Input your sytem value here
60 | Initial Temperature | Input your initial system temperature here
160 | Max Temp | Input your systems maximum temperature here
0.02037 | Expansion Factor | Constant Based on Temp Change ( value will auto fill in )
18.333 | Expanded Water Volume
30 | Min Pressure
60 | Max Pressure
0.402 | Acceptance Factor | Based on cell Min Pressure & Max Pressure ( value will auto fill in )
45.6045 | Tank Volume Required | If cell to left is N/A use tank value to right |  |  |  | 45.6492
Tank model
Max Temp | Initial Temperature
| 40 | 45 | 50 | 55 | 60 | 65 | 70 | 75 | 80 | 85 | 90 | 95 | 100
50 | 6e-05 | 8e-05
55 | 0.00025 | 0.00027 | 0.00019
60 | 0.00055 | 0.00057 | 0.00049 | 0.0003
65 | 0.00093 | 0.00095 | 0.00087 | 0.00068 | 0.00038
70 | 0.00149 | 0.00151 | 0.00143 | 0.00124 | 0.00094 | 0.00056
75 | 0.00194 | 0.00196 | 0.00188 | 0.00169 | 0.00139 | 0.00101 | 0.00045
80 | 0.0026 | 0.00262 | 0.00254 | 0.00235 | 0.00205 | 0.00167 | 0.00111 | 0.00066
85 | 0.00326 | 0.00328 | 0.0032 | 0.00301 | 0.00271 | 0.00233 | 0.00177 | 0.00132 | 0.00066
90 | 0.00405 | 0.00407 | 0.00399 | 0.0038 | 0.0035 | 0.00312 | 0.00256 | 0.00211 | 0.00145 | 0.00079
95 | 0.00485 | 0.00487 | 0.00479 | 0.0046 | 0.0043 | 0.00392 | 0.00336 | 0.00291 | 0.00225 | 0.00159 | 0.0008
100 | 0.00575 | 0.00577 | 0.00569 | 0.0055 | 0.0052 | 0.00482 | 0.00426 | 0.00381 | 0.00315 | 0.00249 | 0.0017 | 0.0009
105 | 0.00671 | 0.00672 | 0.00665 | 0.00646 | 0.00616 | 0.00578 | 0.00522 | 0.00477 | 0.00411 | 0.00345 | 0.00266 | 0.00186 | 0.00096
110 | 0.00771 | 0.00773 | 0.00765 | 0.00746 | 0.00716 | 0.00678 | 0.00622 | 0.00577 | 0.00511 | 0.00445 | 0.00366 | 0.00286 | 0.00196
115 | 0.00879 | 0.00881 | 0.00873 | 0.00854 | 0.00824 | 0.00786 | 0.0073 | 0.00685 | 0.00619 | 0.00553 | 0.00474 | 0.00394 | 0.00304
120 | 0.01004 | 0.01006 | 0.00998 | 0.00979 | 0.00949 | 0.00911 | 0.00855 | 0.0081 | 0.00744 | 0.00678 | 0.00599 | 0.00519 | 0.00429
125 | 0.01111 | 0.0113 | 0.01105 | 0.01086 | 0.01056 | 0.01018 | 0.00962 | 0.00917 | 0.00851 | 0.00785 | 0.00706 | 0.00625 | 0.00536
130 | 0.01236 | 0.01238 | 0.0123 | 0.01211 | 0.01181 | 0.01143 | 0.01087 | 0.01042 | 0.00976 | 0.0091 | 0.00831 | 0.00751 | 0.00661
135 | 0.01368 | 0.0137 | 0.03162 | 0.01342 | 0.01313 | 0.01275 | 0.01219 | 0.01174 | 0.01108 | 0.01042 | 0.00963 | 0.00883 | 0.00793
140 | 0.01501 | 0.01503 | 0.01495 | 0.01476 | 0.01446 | 0.01408 | 0.01352 | 0.01307 | 0.01241 | 0.01175 | 0.01096 | 0.01016 | 0.00926
145 | 0.01643 | 0.01645 | 0.01637 | 0.01618 | 0.01588 | 0.0155 | 0.01494 | 0.01449 | 0.01383 | 0.01317 | 0.01238 | 0.01158 | 0.01068
150 | 0.01787 | 0.01787 | 0.01779 | 0.0176 | 0.0173 | 0.01692 | 0.01636 | 0.01591 | 0.01525 | 0.01459 | 0.0133 | 0.013 | 0.0121
155 | 0.01937 | 0.01939 | 0.01931 | 0.01912 | 0.01882 | 0.01844 | 0.01788 | 0.01743 | 0.01677 | 0.01611 | 0.01532 | 0.01452 | 0.01362
160 | 0.02092 | 0.02094 | 0.02086 | 0.02067 | 0.02037 | 0.01999 | 0.01943 | 0.01877 | 0.01811 | 0.01732 | 0.01652 | 0.01572 | 0.01482
165 | 0.02252 | 0.02254 | 0.02246 | 0.02227 | 0.01297 | 0.02159 | 0.02103 | 0.02058 | 0.01992 | 0.01926 | 0.01847 | 0.01767 | 0.01677
170 | 0.02418 | 0.0242 | 0.02412 | 0.02393 | 0.02363 | 0.02325 | 0.02269 | 0.02224 | 0.02158 | 0.02092 | 0.02013 | 0.01933 | 0.01843
175 | 0.02588 | 0.0259 | 0.02582 | 0.02563 | 0.02533 | 0.02495 | 0.02439 | 0.02394 | 0.02328 | 0.02262 | 0.02183 | 0.02103 | 0.02013
180 | 0.02763 | 0.02765 | 0.02757 | 0.02738 | 0.02708 | 0.0267 | 0.02614 | 0.02569 | 0.02503 | 0.02437 | 0.02358 | 0.02278 | 0.02188
185 | 0.02941 | 0.02943 | 0.02935 | 0.02916 | 0.02886 | 0.02848 | 0.02792 | 0.02747 | 0.02681 | 0.02615 | 0.02536 | 0.02456 | 0.02366
190 | 0.03127 | 0.03129 | 0.03121 | 0.03102 | 0.03072 | 0.03034 | 0.02978 | 0.02933 | 0.02867 | 0.02801 | 0.02722 | 0.02642 | 0.02552
195 | 0.03314 | 0.03316 | 0.03308 | 0.03289 | 0.03259 | 0.03221 | 0.03165 | 0.0312 | 0.03054 | 0.02988 | 0.02909 | 0.02829 | 0.02739
200 | 0.0351 | 0.03512 | 0.03504 | 0.03485 | 0.03455 | 0.03417 | 0.03361 | 0.03316 | 0.0325 | 0.03184 | 0.03105 | 0.03025 | 0.02935
205 | 0.03707 | 0.03709 | 0.03701 | 0.03682 | 0.03652 | 0.03614 | 0.03558 | 0.03513 | 0.03447 | 0.03381 | 0.03302 | 0.03222 | 0.03132
210 | 0.03911 | 0.03913 | 0.03905 | 0.03885 | 0.03856 | 0.03818 | 0.03762 | 0.03717 | 0.03651 | 0.03585 | 0.03506 | 0.03426 | 0.03336
215 | 0.0412 | 0.04122 | 0.04114 | 0.04095 | 0.04065 | 0.04027 | 0.03971 | 0.03926 | 0.0386 | 0.03794 | 0.03715 | 0.03635 | 0.03545
220 | 0.04335 | 0.04337 | 0.04329 | 0.0431 | 0.0428 | 0.04242 | 0.04186 | 0.04141 | 0.04075 | 0.04009 | 0.0393 | 0.0385 | 0.0376
225 | 0.04549 | 0.04551 | 0.04543 | 0.04524 | 0.04494 | 0.04456 | 0.044 | 0.04355 | 0.04289 | 0.04223 | 0.04144 | 0.04064 | 0.03974
230 | 0.04762 | 0.04764 | 0.04756 | 0.04737 | 0.04707 | 0.04669 | 0.04613 | 0.04568 | 0.04502 | 0.04436 | 0.04357 | 0.04277 | 0.04187
235 | 0.04991 | 0.04993 | 0.04985 | 0.04966 | 0.04936 | 0.04898 | 0.04812 | 0.04797 | 0.04731 | 0.04665 | 0.04586 | 0.04506 | 0.04416
240 | 0.0522 | 0.05222 | 0.05214 | 0.05195 | 0.05165 | 0.05127 | 0.05071 | 0.05026 | 0.0496 | 0.04894 | 0.04815 | 0.04735 | 0.04645
Acceptance Factors
Max Pressure P0 | Min Pressure at tank PSIG P1
PSIG | 5 | 10 | 12 | 15 | 20 | 25 | 30 | 35 | 40 | 45 | 50
30 | 0.56 | 0.477 | 0.403 | 0.336 | 0.224 | 0.112
40 | 0.64 | 0.548 | 0.512 | 0.457 | 0.366 | 0.274 | 0.183 | 0.091 |  |  |  | If pressures exceed table, use formula:
50 | 0.696 | 0.618 | 0.587 | 0.541 | 0.464 | 0.386 | 0.309 | 0.232 | 0.155 | 0.078
60 | 0.736 | 0.669 | 0.643 | 0.602 | 0.59 | 0.469 | 0.402 | 0.335 | 0.268 | 0.201 | 0.134 | 1 - | P1+14.7
70 | 0.767 | 0.708 | 0.685 | 0.649 | 0.634 | 0.531 | 0.472 | 0.413 | 0.354 | 0.295 | 0.236 |  | P0+14.7
80 | 0.792 | 0.739 | 0.718 | 0.686 | 0.669 | 0.581 | 0.528 | 0.475 | 0.422 | 0.37 | 0.317
90 | 0.812 | 0.764 | 0.745 | 0.716 | 0.698 | 0.621 | 0.573 | 0.525 | 0.478 | 0.43 | 0.382 | P1 | 30
100 | 0.828 | 0.785 | 0.767 | 0.741 | 0.723 | 0.654 | 0.61 | 0.567 | 0.523 | 0.479 | 0.436 | P0 | 60
110 | 0.842 | 0.802 | 0.786 | 0.762 | 0.723 | 0.682 | 0.642 | 0.601 | 0.561 | 0.521 | 0.481
120 | 0.854 | 0.817 | 0.802 | 0.78 | 0.742 | 0.705 | 0.668 | 0.631 | 0.594 | 0.557 | 0.52 | 0.40161
125 | 0.859 | 0.823 | 0.809 | 0.787 | 0.752 | 0.716 | 0.68 | 0.644 | 0.608 | 0.573 | 0.537

## Metric Calculations
3406.8708 | Sys Vol (liters) | Input your sytem value here
15.5556 | Initial Temperature celcius | Input your initial system temperature here
71.1111 | Max Temp | Input your systems maximum temperature here
0.077109 | Expansion Factor | Constant Based on Temp Change ( value will auto fill in )
262.6999 | Expanded Water Volume
146.4729 | Min Pressure (kg/m2)
292.9457 | Max Pressure (Kg/m2)
0.402 | Acceptance Factor | Based on cell Min Pressure & Max Pressure ( value will auto fill in )
172.6317 | Tank Volume Required (liters)
Tank model